## Slide 1: Summit Cooling and Environmental Control Jeff Barr Project Architect Oscar Nuñez Facility Technical Coordinator German Schumacher Software Engineering Lead LSST 2017 Project & Community Workshop August 15, 2017

## Slide 2: Cooling Ventilation Air Conditioning (CVAC)
CVAC provides the cooling capacity to condition enclosure temperature during daytime cycle, to extract heat from mirrors cells and other heat sources, and to condition/ventilate the enclosed areas of the Service Building
Installation schedule included in Summit Construction Contract Program (Gantt Chart):
  Process includes purchasing, fabrication & integration of all equipment.
  Masterclima – subcontractor to Besalco – will complete work in October
Verification and Acceptance Process,
  According to Specifications in the Contract and Document 17368
  Masterclima is reportedly developing a plan for appropriate testing which they will submit to us for review
  We need to proactively provide them with input on the critical testing and verification we will require for CVAC equipment and its control

## Slide 3: Summit Facility Environmental Control Zoning
camera shop
air exhaust
receiving
mirror coating
platform lift shaft
telescope pier
Control Room, Computing, Offices – Air Conditioned
Service Building – Particulate Controlled Ambient Temperature (w/ minimal conditioning)
Lift Shaft – Ambient Ventilation
Inside Telescope Enclosure: Daytime – Active Air Conditioning (to nighttime startup temp.)
Nighttime – Natural Ventilation (w/ supplemental active downdraft)
56 m length (x 24m width)
25 m
37.8 m
Thermal Management Plan: Doc. LTS-106
30 m diameter
Camera Clean and White Rooms (beyond) – particulate, temperature and humidity control
Utility Equipment – Natural & Active Ventilation

## Slide 4: Thermal Management of the Enclosure
The Summit Facility will be under thermal management, with the implementation of an Enclosure Environment Conditioning system (EEC), that will condition the different sections of the Summit Facility, according to its functionality.
To minimize dome seeing at the beginning of observing (daytime cycle), the interior temperature of the enclosure and the telescope, will be maintained while the dome is closed at a temperature appropriate when opening for observing.
When observing (nighttime cycle), the temperature of the telescope and enclosure are controlled by wind flushing through the enclosure vents and enclosure slits, along with a down draft system.

## Slide 5: Current Progress with Summit Environmental Control System Avance del SISTEMA de Control de Clima en la Montaña

## Slide 6: Current Progress – Mechanical Room & Chillers
3 Main Chillers - view from outside south end of building

## Slide 7: Se aprecia la conexion de las tuberias de alimentacion y retorno hacia los chiller que se encuentra incompleta
Current Progress – Manifolds & Piping

## Slide 8: Current Progress – Glycol Supply and Return
MANIFOLD DE ALIMENTACION Y RETORNO A LA SALIDA DE LOS CHILLER
Provide for interchangeability of low-temp. and standard building chillers.

## Slide 9: Se puede apreciar la instalacion de los manifold y la union entre dos de ellos que son los que alimentan a clima telescopio
Current Progress – Chillers and Manifolds

## Slide 10: La ruta de las tuberias para clima esta definida por el schaft que se aprecia y que corresponde a la caja escala
Current Progress – Piping & Shaft

## Slide 11
Current Progress – Piping & Shaft

## Slide 12
RUTA CON LAS TUBERIAS DE ALIMETACION HACIA LOS UMAS (INCONCLUSAS)
Current Progress – Horizontal Piping Run

## Slide 13
Current Progress – Horizontal Piping Run

## Slide 14
Current Progress – Main Ventilation Ducts

## Slide 15
Current Progress – Piping to Fan Coils at 2nd Level

## Slide 16
SISTEMA DE INYECCION A OFICINAS QUE SE UNE CON LAS MANGAS DEL LOS FAN-COIL
Current Progress – Fan Coil at Office Area

## Slide 17
Current Progress – Glycol S&R to Fan Coil

## Slide 18
TABLERO DE CONTROL INDIVIDUAL DE CADA SISTEMA DE FAN-COIL Y SENSOR DE PRESION INSTALADO EN DUCTO
Current Progress – Control Unit at Fan Coil

## Slide 19
EQUIPO UMAS A INSTALAR SOBRE SOPORTES
Current Progress – Air Handling Unit for Dome

## Slide 20
Current Progress – Dome AHU Support Platform

## Slide 21: CVAC Control System Specifications and Status

## Slide 22: Proposed Centralized Control For CVAC
- Siemens hardware based on industry standard open protocol.
- Connection to LSST communications for telemetry capture and supervision.
- Training on operations and customization of system.

## Slide 24: EEC Control Architecture
DDS Communications Middleware
Enclosure
Environment
Control
Camera
TCS
CC
Chiller(s)
Air
Handling
Units
Fans
LOUVERS
Enclosure
Sensors
Facility
Database
External
Sensors
Optics
Controller
Mirrors
Thermal
Control
Camera
Thermal
Control
CVAC
DOME
CVAC
Sensors
Flow
Valves
Sensors
Readout
Fans

## Slide 25: Control Architecture from Technical Specifications

## Slide 26: Control Diagram from Technical Specifications

## Slide 27: CVAC Equipment under Centralized Control

## Slide 28: CVAC Equipment under Centralized Control (cont.)

## Slide 29: Example of Equipment Control Diagram

## Slide 30: Imminent Completion of Besalco/Masterclima Contract

## Slide 31: Besalco Current Gantt Chart for Climatización

## Slide 32: Adjustment, Start-up, Commissioning excerpt from Technical Specifications

## Slide 33: Field Performance Testing of Equipment excerpt from Technical Specifications

## Slide 34: Questions to Be Addressed – Today or Soon
What, if any, non-standard mechanical testing do we expect Masterclima to do for the cooling and ventilation equipment?
Can “simulate” the presence of the dome in some way to ensure adequate capacity and proper functioning of AHUs, bi-pass valves, ventilator fans under static pressure, etc?
Do we need to simulate any other load conditions (e.g. mirror cooling, computer room heat load.
What control input/output protocols should we require for testing for all equipment?
What monitoring capability do we expect to have demonstrated prior to acceptance?
We will test the response of the system to the mechanical failure of one of the low temperature chillers, and back-up by the general purpose chiller. Are there any other similar special test conditions we should consider?